CONVERSION MULTIPLIERS

(Thousands of Btu)

(Refer to ASHRAE Standard 105-1984 for unusual fuels)

| Fuel | Measured Units | Conversion Multiplier |
| --- | --- | --- |
| Electricity | KWh MWh | 3.413 3413 |
| Natural Gas | CCF | 103 |
|  | MCF | 1030 |
|  | Therm | 100 |
|  | Cubic Meter | 36.4 |
|  | Gigajoule | 947.8 |
| Purchased Steam | 1000 Btu | 1.0 |
|  | 1000 lb | 1000 |
|  | Therm | 100 |
| Purchased Hot Water | 1000 Btu | 1.0 |
| Purchased Chilled Water | 1000 Btu | 1.0 |
|  | Ton-Hour | 12.0 |
| Oil #2 | U.S. Gallon | 139 |
|  | Imp. Gallon Liter | 167 36.7 |
| Oil #6 | U.S. Gallon | 154 |
|  | Imp. Gallon Liter | 185 40.7 |
| Propane | U.S. Gallon Imp. Gallon Liter | 91.6 110 24.2 |
| Anthracite Coal | Ton | 25,400 |

WATER VOLUME CONVERSION

U.S. Gallons × 0.1337 = ft3

Imperial Gallons × 0.1605 = ft3